## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 32 | 32 | 61 | 175 | 5.97 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 51 | 50 | 42 | 24 | 62.5 | 58.49 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 32 | 33 | 33 | 61 | 198.5 | 5.97 | 50 | 75.6 | 42.4 | 68.7 | 47 | 212.3 | 208.6 | 208.6 | NO
| NG | 50 | 31 | 42 | 24 | 62.5 | 58.41 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
1 | OK | 33 | 34 | 34 | 61 | 235.8 | 4.51 | 50 | 75.6 | 42.4 | 70.4 | 45.9 | 212.2 | 210.2 | 210.2 | YES
| NG | 31 | 13 | 42 | 24 | 62.5 | 55.78 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_B sim: not converged
2 | OK | 34 | 35 | 35 | 61 | 237.9 | 2.68 | 50 | 75.6 | 42.4 | 72.5 | 42.4 | 212.2 | 211.9 | 211.9 | YES
| NG | 13 | 12 | 42 | 24 | 62.5 | 53.72 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_B sim: not converged
| NG | 12 | 11 | 42 | 24 | 62.5 | 36.1 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_B sim: not converged
3 | OK | 12 | 14 | 48 | 25 | 101.7 | 17.16 | 50 | 75.6 | 42.4 | 54.8 | 48 | 213.5 | 211.4 | 211.4 | YES
| NG | 11 | 44 | 42 | 24 | 62.5 | 35.79 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_B sim: not converged
4 | OK | 14 | 30 | 48 | 25 | 101.7 | 17.16 | 50 | 75.6 | 42.4 | 55.3 | 48 | 213.6 | 211.4 | 211.4 | YES
| NG | 44 | 4 | 42 | 24 | 62.5 | 35.79 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_B sim: not converged
| NG | 30 | 52 | 48 | 25 | 101.7 | 17.16 | 50 | 75.6 | 42.4 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 42.4% (degenerate)
| NG | 4 | 5 | 5 | 61 | 131.3 | 17.51 | 50 | 75.6 | 42.4 | 54.5 | 57.9 | 221.4 | 176 | 176 | NO
| NG | 4 | 53 | 42 | 24 | 62.5 | 18.13 | 50 | 75.6 | 42.4 | 54 | 57.5 | 216 | 191.8 | 191.8 | NO
5 | OK | 52 | 41 | 48 | 25 | 101.7 | 17.16 | 50 | 75.6 | 42.4 | 55.3 | 48 | 213.6 | 211.4 | 211.4 | YES
| NG | 5 | 22 | 22 | 61 | 197.7 | 16.93 | 50 | 75.6 | 42.4 | 55.1 | 57.2 | 221.5 | 178.4 | 178.4 | NO
| NG | 53 | 9 | 42 | 24 | 62.5 | 18.13 | 50 | 75.6 | 42.4 | 54 | 57.5 | 216 | 191.8 | 191.8 | NO
6 | OK | 41 | 0 | 48 | 25 | 101.7 | 17.16 | 50 | 75.6 | 42.4 | 55.3 | 48 | 213.6 | 211.4 | 211.4 | YES
| NG | 22 | 2 | 2 | 61 | 232 | 15.57 | 50 | 75.6 | 42.4 | 56.7 | 56.1 | 221 | 179 | 179 | NO
| NG | 9 | 10 | 42 | 24 | 62.5 | 18.13 | 50 | 75.6 | 42.4 | 54 | 57.5 | 216 | 191.8 | 191.8 | NO
7 | OK | 0 | 1 | 48 | 25 | 101.7 | 0.38 | 50 | 75.6 | 42.4 | 74.9 | 42.4 | 212 | 211.9 | 211.9 | YES
8 | OK | 0 | 36 | 36 | 25 | 110.6 | 16.29 | 50 | 75.6 | 42.4 | 56.3 | 47.7 | 213.4 | 211.9 | 211.9 | YES
| NG | 2 | 3 | 3 | 61 | 241.5 | 10.9 | 50 | 75.6 | 42.4 | 62.2 | 52.1 | 220.6 | 182.9 | 182.9 | NO
9 | OK | 2 | 6 | 6 | 61 | 238.7 | 4.67 | 50 | 75.6 | 42.4 | 70 | 46 | 212.9 | 210.6 | 210.6 | YES
10 | OK | 10 | 42 | 42 | 24 | 62.5 | 4.95 | 50 | 75.6 | 42.4 | 69.5 | 46.1 | 215.1 | 211.9 | 211.9 | YES
11 | OK | 10 | 39 | 39 | 24 | 130.3 | 13.18 | 50 | 75.6 | 42.4 | 60 | 44.8 | 212.7 | 211.9 | 211.9 | YES
12 | ** OPTIMAL ** | 36 | 37 | 37 | 27 | 140.1 | 16.29 | 50 | 75.6 | 42.4 | 56.3 | 47.7 | 213.4 | 211.9 | 211.9 | YES
13 | OK | 42 | 45 | 45 | 24 | 98.8 | 4.95 | 50 | 75.6 | 42.4 | 69.5 | 46.1 | 215.1 | 211.9 | 211.9 | YES
14 | OK | 39 | 40 | 40 | 24 | 131.3 | 12.28 | 50 | 75.6 | 42.4 | 61.1 | 44.8 | 212.1 | 211.9 | 211.9 | YES
15 | OK | 37 | 16 | 16 | 27 | 180 | 13.69 | 50 | 75.6 | 42.4 | 59.4 | 46.8 | 213.3 | 211.9 | 211.9 | YES
16 | OK | 45 | 46 | 46 | 24 | 132.1 | 3.64 | 50 | 75.6 | 42.4 | 71.1 | 45.1 | 214.3 | 211.9 | 211.9 | YES
17 | OK | 40 | 47 | 47 | 24 | 152.4 | 6.26 | 50 | 75.6 | 42.4 | 68.1 | 44.8 | 212.7 | 211.9 | 211.9 | YES
18 | OK | 16 | 15 | 15 | 27 | 219 | 9.26 | 50 | 75.6 | 42.4 | 64.6 | 46.3 | 212.7 | 211.9 | 211.9 | YES
19 | OK | 46 | 49 | 49 | 24 | 161.8 | 0.27 | 50 | 75.6 | 42.4 | 75.2 | 42.6 | 212 | 211.9 | 211.9 | YES
20 | OK | 47 | 19 | 19 | 24 | 178.3 | 5.6 | 50 | 75.6 | 42.4 | 68.9 | 44.8 | 212.8 | 211.9 | 211.9 | YES
21 | OK | 15 | 38 | 38 | 27 | 221 | 9.26 | 50 | 75.6 | 42.4 | 64.6 | 46.3 | 212.7 | 211.9 | 211.9 | YES
22 | OK | 19 | 20 | 20 | 24 | 215.2 | 1.27 | 50 | 75.6 | 42.4 | 74 | 42.4 | 212.2 | 211.9 | 211.9 | YES
23 | OK | 20 | 21 | 21 | 24 | 217 | 1.27 | 50 | 75.6 | 42.4 | 74 | 42.4 | 212.2 | 211.9 | 211.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-021240
TR_B (available) | 59-018422
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 75.6
TR_B Baseline Loading% | 42.4
Total Scenarios Evaluated | 40
Feasible Scenarios | 23
--- Optimal Solution ---
Switch Parent Node | 36
Switch Child Node | 37
Tie Node (TR_A side) | 37
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 140.1
Load Transferred (kW) | 16.29
TR_A Loading After (%) | 56.3
TR_B Loading After (%) | 47.7
Minimum Voltage (V) | 211.9