## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 32 | 35 | 11 | 63.4 | 5.97 | 50 | 75.6 | 29.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 32 | 33 | 35 | 11 | 63.4 | 5.97 | 50 | 75.6 | 29.5 | 68.7 | 36.4 | 212.3 | 218.6 | 212.3 | YES
2 | OK | 33 | 34 | 35 | 11 | 63.4 | 4.51 | 50 | 75.6 | 29.5 | 70.4 | 34.7 | 212.2 | 218.9 | 212.2 | YES
3 | OK | 34 | 35 | 35 | 11 | 63.4 | 2.68 | 50 | 75.6 | 29.5 | 72.5 | 29.5 | 212.2 | 219.4 | 212.2 | YES
4 | OK | 12 | 11 | 25 | 12 | 6 | 36.1 | 50 | 75.6 | 29.5 | 32.8 | 72.3 | 222.4 | 210.7 | 210.7 | YES
5 | OK | 12 | 14 | 17 | 11 | 98.1 | 17.16 | 50 | 75.6 | 29.5 | 54.8 | 49.7 | 213.5 | 217 | 213.5 | YES
| NG | 11 | 44 | 25 | 12 | 6 | 35.79 | 50 | 75.6 | 29.5 | 0 | 72 | 6 | 210.6 | 6 | NO
6 | OK | 14 | 30 | 17 | 11 | 98.1 | 17.16 | 50 | 75.6 | 29.5 | 55.3 | 49.7 | 213.6 | 217 | 213.6 | YES
7 | OK | 44 | 4 | 25 | 12 | 6 | 35.79 | 50 | 75.6 | 29.5 | 33.1 | 71.8 | 222.2 | 210.6 | 210.6 | YES
| NG | 30 | 52 | 17 | 11 | 98.1 | 17.16 | 50 | 75.6 | 29.5 | 55.3 | 1155.9 | 213.6 | 41.8 | 41.8 | NO
8 | OK | 4 | 5 | 25 | 12 | 6 | 17.51 | 50 | 75.6 | 29.5 | 54.5 | 49.8 | 221.4 | 218.3 | 218.3 | YES
9 | OK | 4 | 53 | 21 | 8 | 176.7 | 18.13 | 50 | 75.6 | 29.5 | 54 | 38.8 | 216 | 212.3 | 212.3 | YES
10 | OK | 52 | 41 | 17 | 11 | 98.1 | 17.16 | 50 | 75.6 | 29.5 | 55.3 | 49.7 | 213.6 | 217 | 213.6 | YES
11 | OK | 5 | 22 | 25 | 12 | 6 | 16.93 | 50 | 75.6 | 29.5 | 55.1 | 49.1 | 221.5 | 218.3 | 218.3 | YES
12 | OK | 53 | 9 | 21 | 8 | 176.7 | 18.13 | 50 | 75.6 | 29.5 | 54 | 38.8 | 216 | 212.3 | 212.3 | YES
13 | OK | 41 | 0 | 17 | 11 | 98.1 | 17.16 | 50 | 75.6 | 29.5 | 55.3 | 49.7 | 213.6 | 217 | 213.6 | YES
14 | OK | 22 | 2 | 25 | 12 | 6 | 15.57 | 50 | 75.6 | 29.5 | 56.7 | 47.5 | 221 | 218.3 | 218.3 | YES
15 | OK | 9 | 10 | 21 | 8 | 176.7 | 18.13 | 50 | 75.6 | 29.5 | 54 | 38.8 | 216 | 212.3 | 212.3 | YES
16 | OK | 0 | 1 | 1 | 11 | 223.8 | 0.38 | 50 | 75.6 | 29.5 | 74.9 | 29.9 | 212 | 219.4 | 212 | YES
17 | OK | 0 | 36 | 17 | 11 | 98.1 | 16.29 | 50 | 75.6 | 29.5 | 56.3 | 48.7 | 213.4 | 217.1 | 213.4 | YES
18 | OK | 2 | 3 | 25 | 12 | 6 | 10.9 | 50 | 75.6 | 29.5 | 62.2 | 42.1 | 220.6 | 219.2 | 219.2 | YES
19 | OK | 2 | 6 | 26 | 15 | 68.1 | 4.67 | 50 | 75.6 | 29.5 | 70 | 34.8 | 212.9 | 218.9 | 212.9 | YES
20 | OK | 10 | 39 | 21 | 8 | 176.7 | 13.18 | 50 | 75.6 | 29.5 | 60 | 32.6 | 212.7 | 219.4 | 212.7 | YES
21 | OK | 36 | 37 | 17 | 11 | 98.1 | 16.29 | 50 | 75.6 | 29.5 | 56.3 | 48.7 | 213.4 | 217.1 | 213.4 | YES
22 | OK | 3 | 23 | 25 | 12 | 6 | 10.51 | 50 | 75.6 | 29.5 | 62.7 | 41.6 | 220.6 | 219.1 | 219.1 | YES
23 | OK | 6 | 26 | 26 | 15 | 68.1 | 4.07 | 50 | 75.6 | 29.5 | 70.7 | 34.1 | 212.7 | 219 | 212.7 | YES
24 | OK | 39 | 40 | 21 | 8 | 176.7 | 12.28 | 50 | 75.6 | 29.5 | 61.1 | 31.5 | 212.1 | 219.4 | 212.1 | YES
25 | OK | 37 | 16 | 17 | 11 | 98.1 | 13.69 | 50 | 75.6 | 29.5 | 59.4 | 45.5 | 213.3 | 217.7 | 213.3 | YES
26 | ** OPTIMAL ** | 23 | 43 | 25 | 12 | 6 | 9.04 | 50 | 75.6 | 29.5 | 64.5 | 31.4 | 220.5 | 219.3 | 219.3 | YES
27 | OK | 26 | 27 | 29 | 8 | 68.6 | 1.09 | 50 | 75.6 | 29.5 | 74.2 | 30 | 212.4 | 219.4 | 212.4 | YES
28 | OK | 40 | 47 | 21 | 8 | 176.7 | 6.26 | 50 | 75.6 | 29.5 | 68.1 | 31.5 | 212.7 | 219.4 | 212.7 | YES
29 | OK | 16 | 15 | 17 | 11 | 98.1 | 9.26 | 50 | 75.6 | 29.5 | 64.6 | 40.3 | 212.7 | 218.7 | 212.7 | YES
30 | OK | 27 | 28 | 29 | 8 | 68.6 | 1.09 | 50 | 75.6 | 29.5 | 74.2 | 30 | 212.4 | 219.4 | 212.4 | YES
31 | OK | 47 | 19 | 21 | 8 | 176.7 | 5.6 | 50 | 75.6 | 29.5 | 68.9 | 31.5 | 212.8 | 219.4 | 212.8 | YES
32 | OK | 15 | 38 | 17 | 11 | 98.1 | 9.26 | 50 | 75.6 | 29.5 | 64.6 | 40.3 | 212.7 | 218.7 | 212.7 | YES
33 | OK | 28 | 29 | 29 | 8 | 68.6 | 0.85 | 50 | 75.6 | 29.5 | 74.5 | 30 | 212.4 | 219.4 | 212.4 | YES
34 | OK | 19 | 20 | 21 | 8 | 176.7 | 1.27 | 50 | 75.6 | 29.5 | 74 | 30.2 | 212.2 | 219.4 | 212.2 | YES
35 | OK | 38 | 18 | 17 | 11 | 98.1 | 4.49 | 50 | 75.6 | 29.5 | 70.2 | 34.7 | 212.3 | 218.5 | 212.3 | YES
36 | OK | 29 | 8 | 8 | 8 | 84.5 | 0.49 | 50 | 75.6 | 29.5 | 74.9 | 30 | 212.5 | 219.4 | 212.5 | YES
37 | OK | 20 | 21 | 21 | 8 | 176.7 | 1.27 | 50 | 75.6 | 29.5 | 74 | 29.5 | 212.2 | 219.4 | 212.2 | YES
38 | OK | 18 | 17 | 17 | 11 | 98.1 | 3.21 | 50 | 75.6 | 29.5 | 71.8 | 29.5 | 211.6 | 219.4 | 211.6 | YES
39 | OK | 8 | 7 | 7 | 8 | 85.7 | 0.49 | 50 | 75.6 | 29.5 | 74.9 | 29.5 | 212.5 | 219.4 | 212.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-021240
TR_B (available) | 62-001681
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 75.6
TR_B Baseline Loading% | 29.5
Total Scenarios Evaluated | 42
Feasible Scenarios | 39
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 43
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 6
Load Transferred (kW) | 9.04
TR_A Loading After (%) | 64.5
TR_B Loading After (%) | 31.4
Minimum Voltage (V) | 219.3