## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 54 | 44 | 3 | 38.3 | 27.62 | 50 | 76.8 | 25 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 55 | 59 | 41 | 0 | 1.2 | 36.99 | 50 | 76.8 | 25 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 54 | 18 | 44 | 3 | 38.3 | 26.3 | 50 | 76.8 | 25 | 46.1 | 39.5 | 209.2 | 179.3 | 179.3 | NO
| NG | 59 | 58 | 41 | 0 | 1.2 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.4 | 220.7 | 198.2 | 198.2 | NO
| NG | 18 | 17 | 44 | 3 | 38.3 | 5.37 | 50 | 76.8 | 25 | 70.6 | 27.6 | 208.2 | 211.9 | 208.2 | NO
| NG | 18 | 53 | 53 | 0 | 89.2 | 20.93 | 50 | 76.8 | 25 | 52.3 | 36.5 | 208.8 | 185.4 | 185.4 | NO
| NG | 58 | 42 | 41 | 0 | 1.2 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.4 | 220.7 | 198.2 | 198.2 | NO
| NG | 17 | 48 | 44 | 3 | 38.3 | 5.37 | 50 | 76.8 | 25 | 70.6 | 27.6 | 208.2 | 211.9 | 208.2 | NO
| NG | 53 | 50 | 50 | 0 | 103.9 | 20.93 | 50 | 76.8 | 25 | 52.3 | 36.6 | 208.8 | 185 | 185 | NO
| NG | 42 | 41 | 41 | 0 | 1.2 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.4 | 220.7 | 198.2 | 198.2 | NO
| NG | 48 | 47 | 44 | 3 | 38.3 | 5.37 | 50 | 76.8 | 25 | 70.6 | 27.6 | 208.2 | 211.9 | 208.2 | NO
| NG | 50 | 49 | 49 | 0 | 121.8 | 20.93 | 50 | 76.8 | 25 | 52.3 | 36.6 | 208.8 | 184.6 | 184.6 | NO
| NG | 41 | 43 | 43 | 0 | 3.2 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.4 | 220.7 | 198.2 | 198.2 | NO
| NG | 47 | 46 | 44 | 3 | 38.3 | 3.36 | 50 | 76.8 | 25 | 72.5 | 26.6 | 208.2 | 211.5 | 208.2 | NO
| NG | 49 | 16 | 16 | 0 | 126.9 | 20.93 | 50 | 76.8 | 25 | 52.3 | 36.6 | 208.8 | 184.4 | 184.4 | NO
| NG | 43 | 0 | 0 | 0 | 20.5 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.4 | 220.7 | 198.2 | 198.2 | NO
| NG | 46 | 45 | 44 | 3 | 38.3 | 0.08 | 50 | 76.8 | 25 | 76.7 | 25.1 | 207.9 | 211.2 | 207.9 | NO
| NG | 16 | 15 | 15 | 0 | 147.8 | 20.93 | 50 | 76.8 | 25 | 52.3 | 36.6 | 208.8 | 184.4 | 184.4 | NO
| NG | 0 | 1 | 1 | 0 | 39.3 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.4 | 220.7 | 198.2 | 198.2 | NO
| NG | 1 | 2 | 35 | 22 | 53.4 | 36.99 | 50 | 76.8 | 25 | 32.1 | 44.5 | 220.7 | 197.2 | 197.2 | NO
| NG | 2 | 3 | 35 | 22 | 53.4 | 31.97 | 50 | 76.8 | 25 | 37.9 | 41.6 | 220.7 | 201.5 | 201.5 | NO
| NG | 3 | 51 | 35 | 22 | 53.4 | 30.71 | 50 | 76.8 | 25 | 39.4 | 40.9 | 220.7 | 201.9 | 201.9 | NO
| NG | 51 | 33 | 35 | 22 | 53.4 | 30.71 | 50 | 76.8 | 25 | 39.4 | 40.9 | 220.7 | 201.9 | 201.9 | NO
| NG | 33 | 34 | 35 | 22 | 53.4 | 27.52 | 50 | 76.8 | 25 | 43 | 39.1 | 220 | 201.5 | 201.5 | NO
| NG | 34 | 35 | 35 | 22 | 53.4 | 25.72 | 50 | 76.8 | 25 | 45.1 | 38.1 | 220 | 201.3 | 201.3 | NO
| NG | 35 | 24 | 24 | 22 | 84.8 | 8.97 | 50 | 76.8 | 25 | 65.5 | 29.3 | 209.5 | 211.7 | 209.5 | NO
| NG | 35 | 36 | 36 | 19 | 53.6 | 15.78 | 50 | 76.8 | 25 | 56.3 | 33.3 | 210.6 | 196.6 | 196.6 | NO
1 | OK | 24 | 25 | 25 | 23 | 117.2 | 7.26 | 50 | 76.8 | 25 | 67.5 | 28.4 | 210.1 | 211.6 | 210.1 | YES
| NG | 36 | 39 | 39 | 21 | 57.3 | 12.01 | 50 | 76.8 | 25 | 61.8 | 31.1 | 211.3 | 204.7 | 204.7 | NO
2 | OK | 39 | 37 | 37 | 21 | 58.1 | 7.69 | 50 | 76.8 | 25 | 67 | 28.8 | 211.2 | 211.4 | 211.2 | YES
3 | ** OPTIMAL ** | 37 | 23 | 23 | 21 | 72.9 | 7.69 | 50 | 76.8 | 25 | 67 | 28.8 | 211.2 | 211.4 | 211.2 | YES
| NG | 23 | 22 | 22 | 21 | 75.3 | 5.13 | 50 | 76.8 | 25 | 70.4 | 26.8 | 207.1 | 210.5 | 207.1 | NO
| NG | 22 | 21 | 21 | 21 | 79.2 | 2.7 | 50 | 76.8 | 25 | 73.4 | 26.4 | 207.4 | 210.1 | 207.4 | NO
| NG | 21 | 20 | 20 | 21 | 84.4 | 1.83 | 50 | 76.8 | 25 | 74.4 | 25.9 | 207.6 | 211.6 | 207.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 67-031399
TR_B (available) | 67-010726
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 76.8
TR_B Baseline Loading% | 25
Total Scenarios Evaluated | 34
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 37
Switch Child Node | 23
Tie Node (TR_A side) | 23
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 72.9
Load Transferred (kW) | 7.69
TR_A Loading After (%) | 67
TR_B Loading After (%) | 28.8
Minimum Voltage (V) | 211.2