## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 54 | 19 | 19 | 47.6 | 27.62 | 50 | 76.8 | 51.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 55 | 59 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 54 | 18 | 19 | 19 | 47.6 | 26.3 | 50 | 76.8 | 51.9 | 46.1 | 58.9 | 209.2 | 193.7 | 193.7 | NO
1 | OK | 59 | 58 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 18 | 53 | 19 | 19 | 47.6 | 20.93 | 50 | 76.8 | 51.9 | 52.3 | 55.4 | 208.8 | 207.9 | 207.9 | NO
2 | OK | 58 | 42 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 53 | 50 | 19 | 19 | 47.6 | 20.93 | 50 | 76.8 | 51.9 | 52.3 | 55.4 | 208.8 | 207.9 | 207.9 | NO
3 | OK | 42 | 41 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 50 | 49 | 19 | 19 | 47.6 | 20.93 | 50 | 76.8 | 51.9 | 52.3 | 55.4 | 208.8 | 207.9 | 207.9 | NO
4 | OK | 41 | 43 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 49 | 16 | 19 | 19 | 47.6 | 20.93 | 50 | 76.8 | 51.9 | 52.3 | 55.4 | 208.8 | 207.9 | 207.9 | NO
5 | OK | 43 | 0 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 16 | 15 | 19 | 19 | 47.6 | 20.93 | 50 | 76.8 | 51.9 | 52.3 | 55.4 | 208.8 | 207.9 | 207.9 | NO
6 | OK | 0 | 1 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 15 | 14 | 19 | 19 | 47.6 | 19.9 | 50 | 76.8 | 51.9 | 53.5 | 54.7 | 208.8 | 210.3 | 208.8 | NO
7 | OK | 1 | 2 | 40 | 15 | 4.4 | 36.99 | 50 | 76.8 | 51.9 | 32.1 | 79.4 | 220.7 | 212.4 | 212.4 | YES
| NG | 14 | 13 | 19 | 19 | 47.6 | 19.9 | 50 | 76.8 | 51.9 | 53.5 | 54.7 | 208.8 | 210.3 | 208.8 | NO
8 | OK | 2 | 3 | 40 | 15 | 4.4 | 31.97 | 50 | 76.8 | 51.9 | 37.9 | 75.5 | 220.7 | 212.4 | 212.4 | YES
| NG | 13 | 30 | 19 | 19 | 47.6 | 19.9 | 50 | 76.8 | 51.9 | 53.5 | 54.7 | 208.8 | 210.3 | 208.8 | NO
9 | OK | 3 | 51 | 40 | 15 | 4.4 | 30.71 | 50 | 76.8 | 51.9 | 39.4 | 74.5 | 220.7 | 212.4 | 212.4 | YES
| NG | 30 | 31 | 19 | 19 | 47.6 | 11.25 | 50 | 76.8 | 51.9 | 63.5 | 54.7 | 208.4 | 210.3 | 208.4 | NO
10 | OK | 51 | 33 | 40 | 15 | 4.4 | 30.71 | 50 | 76.8 | 51.9 | 39.4 | 74.5 | 220.7 | 212.4 | 212.4 | YES
| NG | 31 | 6 | 19 | 19 | 47.6 | 8.27 | 50 | 76.8 | 51.9 | 67.1 | 54.3 | 208.4 | 211.4 | 208.4 | NO
11 | ** OPTIMAL ** | 33 | 34 | 40 | 15 | 4.4 | 27.52 | 50 | 76.8 | 51.9 | 43 | 72.2 | 220 | 212.8 | 212.8 | YES
| NG | 6 | 7 | 19 | 19 | 47.6 | 4.71 | 50 | 76.8 | 51.9 | 71.2 | 53.7 | 208.1 | 213.2 | 208.1 | NO
12 | OK | 34 | 35 | 40 | 15 | 4.4 | 25.72 | 50 | 76.8 | 51.9 | 45.1 | 70.8 | 220 | 212.8 | 212.8 | YES
| NG | 7 | 8 | 19 | 19 | 47.6 | 4.6 | 50 | 76.8 | 51.9 | 71.4 | 53.6 | 208.1 | 213.4 | 208.1 | NO
| NG | 35 | 24 | 25 | 6 | 39.5 | 8.97 | 50 | 76.8 | 51.9 | 65.5 | 59.8 | 209.5 | 199 | 199 | NO
13 | OK | 35 | 36 | 40 | 15 | 4.4 | 15.78 | 50 | 76.8 | 51.9 | 56.3 | 63.4 | 210.6 | 212.9 | 210.6 | YES
| NG | 8 | 4 | 19 | 19 | 47.6 | 4.41 | 50 | 76.8 | 51.9 | 71.6 | 53.5 | 208.1 | 213.6 | 208.1 | NO
| NG | 24 | 25 | 25 | 6 | 39.5 | 7.26 | 50 | 76.8 | 51.9 | 67.5 | 58.2 | 210.1 | 202 | 202 | NO
14 | OK | 36 | 39 | 40 | 15 | 4.4 | 12.01 | 50 | 76.8 | 51.9 | 61.8 | 60.7 | 211.3 | 213 | 211.3 | YES
| NG | 4 | 5 | 19 | 19 | 47.6 | 1.95 | 50 | 76.8 | 51.9 | 74.5 | 53.5 | 207.9 | 213.6 | 207.9 | NO
| NG | 4 | 9 | 9 | 19 | 62.4 | 2.46 | 50 | 76.8 | 51.9 | 73.8 | 51.9 | 208.1 | 213.2 | 208.1 | NO
15 | OK | 39 | 37 | 40 | 15 | 4.4 | 7.69 | 50 | 76.8 | 51.9 | 67 | 57.5 | 211.2 | 213 | 211.2 | YES
| NG | 9 | 10 | 10 | 19 | 68.9 | 1.68 | 50 | 76.8 | 51.9 | 74.8 | 51.9 | 208.1 | 213.2 | 208.1 | NO
16 | OK | 37 | 23 | 20 | 15 | 19.8 | 7.69 | 50 | 76.8 | 51.9 | 67 | 57.5 | 211.2 | 213 | 211.2 | YES
| NG | 10 | 11 | 11 | 19 | 74.3 | 1.03 | 50 | 76.8 | 51.9 | 75.6 | 51.9 | 208.1 | 213.2 | 208.1 | NO
| NG | 23 | 22 | 20 | 15 | 19.8 | 5.13 | 50 | 76.8 | 51.9 | 70.4 | 54.4 | 207.1 | 213 | 207.1 | NO
| NG | 22 | 21 | 20 | 15 | 19.8 | 2.7 | 50 | 76.8 | 51.9 | 73.4 | 53.9 | 207.4 | 213 | 207.4 | NO
| NG | 21 | 20 | 20 | 15 | 19.8 | 1.83 | 50 | 76.8 | 51.9 | 74.4 | 53.3 | 207.6 | 213.1 | 207.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 67-031399
TR_B (available) | 67-028715
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 76.8
TR_B Baseline Loading% | 51.9
Total Scenarios Evaluated | 41
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 34
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 15
Tie Line Distance (m) | 4.4
Load Transferred (kW) | 27.52
TR_A Loading After (%) | 43
TR_B Loading After (%) | 72.2
Minimum Voltage (V) | 212.8