## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 82 | 81 | 32 | 22 | 34.6 | 16.81 | 50 | 92.2 | 46.4 | 70.1 | 67.4 | 202.5 | 201.5 | 201.5 | NO
| NG | 82 | 67 | 23 | 16 | 37.3 | 26.86 | 50 | 92.2 | 46.4 | 59.6 | 72.9 | 211.1 | 181.6 | 181.6 | NO
| NG | 81 | 62 | 32 | 22 | 34.6 | 16.81 | 50 | 92.2 | 46.4 | 72.2 | 67.4 | 202.6 | 201.5 | 201.5 | NO
| NG | 67 | 68 | 23 | 16 | 37.3 | 25.78 | 50 | 92.2 | 46.4 | 60.9 | 72.9 | 210.3 | 181.6 | 181.6 | NO
| NG | 62 | 15 | 32 | 22 | 34.6 | 13.86 | 50 | 92.2 | 46.4 | 75.6 | 63.6 | 202.8 | 204.5 | 202.8 | NO
| NG | 68 | 77 | 23 | 16 | 37.3 | 25.78 | 50 | 92.2 | 46.4 | 60.9 | 72.9 | 210.3 | 181.6 | 181.6 | NO
| NG | 77 | 51 | 23 | 16 | 37.3 | 23.8 | 50 | 92.2 | 46.4 | 63.2 | 72.9 | 210.3 | 181.6 | 181.6 | NO
1 | ** OPTIMAL ** | 51 | 52 | 52 | 21 | 90.1 | 12.25 | 50 | 92.2 | 46.4 | 76.8 | 61.4 | 210.7 | 210 | 210 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-031800
TR_B (available) | 28-000860
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 92.2
TR_B Baseline Loading% | 46.4
Total Scenarios Evaluated | 8
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 51
Switch Child Node | 52
Tie Node (TR_A side) | 52
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 90.1
Load Transferred (kW) | 12.25
TR_A Loading After (%) | 76.8
TR_B Loading After (%) | 61.4
Minimum Voltage (V) | 210