## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 75 | 21 | 41 | 4.9 | 54.71 | 50 | 92.2 | 24.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 74 | 63 | 85 | 38 | 7.8 | 22.73 | 50 | 92.2 | 24.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 75 | 76 | 21 | 41 | 4.9 | 54.15 | 50 | 92.2 | 24.8 | 27.5 | 74.5 | 219.9 | 144.8 | 144.8 | NO
| NG | 63 | 7 | 85 | 38 | 7.8 | 21.62 | 50 | 92.2 | 24.8 | 66.8 | 41.5 | 204.1 | 206.6 | 204.1 | NO
| NG | 76 | 84 | 21 | 41 | 4.9 | 52.39 | 50 | 92.2 | 24.8 | 29.5 | 72 | 219.7 | 151.6 | 151.6 | NO
| NG | 7 | 71 | 85 | 38 | 7.8 | 20.8 | 50 | 92.2 | 24.8 | 66.9 | 40.9 | 204.1 | 206.4 | 204.1 | NO
| NG | 84 | 79 | 21 | 41 | 4.9 | 52.39 | 50 | 92.2 | 24.8 | 29.5 | 71.1 | 219.7 | 155.2 | 155.2 | NO
| NG | 71 | 19 | 85 | 38 | 7.8 | 19.42 | 50 | 92.2 | 24.8 | 69.4 | 39.9 | 203.5 | 206 | 203.5 | NO
| NG | 79 | 78 | 21 | 41 | 4.9 | 51.39 | 50 | 92.2 | 24.8 | 30 | 69.8 | 219.7 | 158.6 | 158.6 | NO
| NG | 78 | 45 | 21 | 41 | 4.9 | 51.39 | 50 | 92.2 | 24.8 | 30.7 | 69.3 | 219.6 | 159.7 | 159.7 | NO
| NG | 45 | 80 | 21 | 41 | 4.9 | 46.89 | 50 | 92.2 | 24.8 | 35.8 | 65 | 218.9 | 171.5 | 171.5 | NO
| NG | 80 | 82 | 21 | 41 | 4.9 | 45.98 | 50 | 92.2 | 24.8 | 36.9 | 62.4 | 218.9 | 178.1 | 178.1 | NO
| NG | 82 | 81 | 81 | 41 | 145.9 | 16.81 | 50 | 92.2 | 24.8 | 70.1 | 39.3 | 202.5 | 181.7 | 181.7 | NO
| NG | 82 | 67 | 21 | 41 | 4.9 | 26.86 | 50 | 92.2 | 24.8 | 59.6 | 46.1 | 211.1 | 188.2 | 188.2 | NO
| NG | 67 | 68 | 21 | 41 | 4.9 | 25.78 | 50 | 92.2 | 24.8 | 60.9 | 46.1 | 210.3 | 188.2 | 188.2 | NO
| NG | 68 | 77 | 21 | 41 | 4.9 | 25.78 | 50 | 92.2 | 24.8 | 60.9 | 46.1 | 210.3 | 188.2 | 188.2 | NO
| NG | 77 | 51 | 21 | 41 | 4.9 | 23.8 | 50 | 92.2 | 24.8 | 63.2 | 44.7 | 210.3 | 187.1 | 187.1 | NO
1 | ** OPTIMAL ** | 51 | 52 | 53 | 41 | 90 | 12.25 | 50 | 92.2 | 24.8 | 76.8 | 34.2 | 210.7 | 211.7 | 210.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-031800
TR_B (available) | 38-020847
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 92.2
TR_B Baseline Loading% | 24.8
Total Scenarios Evaluated | 18
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 51
Switch Child Node | 52
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 41
Tie Line Distance (m) | 90
Load Transferred (kW) | 12.25
TR_A Loading After (%) | 76.8
TR_B Loading After (%) | 34.2
Minimum Voltage (V) | 210.7