## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 75 | 78 | 27 | 2 | 54.71 | 50 | 92.2 | 10.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 74 | 63 | 63 | 8 | 49.5 | 22.73 | 95 | 92.2 | 10.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 75 | 76 | 78 | 27 | 2 | 54.15 | 50 | 92.2 | 10.4 | 27.5 | 37.3 | 219.9 | 195.2 | 195.2 | NO
| NG | 63 | 7 | 7 | 8 | 51.6 | 21.62 | 95 | 92.2 | 10.4 | 66.8 | 21.2 | 204.1 | 205.4 | 204.1 | NO
| NG | 76 | 84 | 78 | 27 | 2 | 52.39 | 50 | 92.2 | 10.4 | 29.5 | 36.4 | 219.7 | 194.9 | 194.9 | NO
| NG | 7 | 71 | 71 | 8 | 73.4 | 20.8 | 95 | 92.2 | 10.4 | 66.9 | 20.9 | 204.1 | 205.1 | 204.1 | NO
| NG | 84 | 79 | 78 | 27 | 2 | 52.39 | 50 | 92.2 | 10.4 | 29.5 | 36.2 | 219.7 | 194.9 | 194.9 | NO
| NG | 71 | 19 | 30 | 8 | 89.9 | 19.42 | 50 | 92.2 | 10.4 | 69.4 | 20 | 203.5 | 202.3 | 202.3 | NO
| NG | 79 | 78 | 78 | 27 | 2 | 51.39 | 50 | 92.2 | 10.4 | 30 | 35.7 | 219.7 | 194.7 | 194.7 | NO
| NG | 78 | 45 | 45 | 27 | 4.2 | 51.39 | 50 | 92.2 | 10.4 | 30.7 | 35.4 | 219.6 | 194.8 | 194.8 | NO
| NG | 45 | 80 | 80 | 27 | 14.6 | 46.89 | 50 | 92.2 | 10.4 | 35.8 | 33.6 | 218.9 | 195.2 | 195.2 | NO
| NG | 80 | 82 | 82 | 27 | 18.7 | 45.98 | 50 | 92.2 | 10.4 | 36.9 | 32.4 | 218.9 | 194.9 | 194.9 | NO
| NG | 82 | 81 | 81 | 27 | 27.1 | 16.81 | 50 | 92.2 | 10.4 | 70.1 | 18.4 | 202.5 | 213.7 | 202.5 | NO
| NG | 82 | 67 | 67 | 27 | 33 | 26.86 | 50 | 92.2 | 10.4 | 59.6 | 23.5 | 211.1 | 192.4 | 192.4 | NO
| NG | 81 | 62 | 11 | 24 | 30.7 | 16.81 | 50 | 92.2 | 10.4 | 72.2 | 15.3 | 202.6 | 223.6 | 202.6 | NO
| NG | 67 | 68 | 68 | 27 | 33.9 | 25.78 | 50 | 92.2 | 10.4 | 60.9 | 23.5 | 210.3 | 192.5 | 192.5 | NO
| NG | 62 | 15 | 11 | 24 | 30.7 | 13.86 | 50 | 92.2 | 10.4 | 75.6 | 14.5 | 202.8 | 225.2 | 202.8 | NO
| NG | 68 | 77 | 77 | 27 | 49.6 | 25.78 | 50 | 92.2 | 10.4 | 60.9 | 23.4 | 210.3 | 193.6 | 193.6 | NO
| NG | 77 | 51 | 54 | 27 | 61.1 | 23.8 | 50 | 92.2 | 10.4 | 63.2 | 22.5 | 210.3 | 193.1 | 193.1 | NO
1 | ** OPTIMAL ** | 51 | 52 | 54 | 27 | 61.1 | 12.25 | 50 | 92.2 | 10.4 | 76.8 | 16.2 | 210.7 | 218.8 | 210.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-031800
TR_B (available) | 60-000270
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 92.2
TR_B Baseline Loading% | 10.4
Total Scenarios Evaluated | 20
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 51
Switch Child Node | 52
Tie Node (TR_A side) | 54
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 61.1
Load Transferred (kW) | 12.25
TR_A Loading After (%) | 76.8
TR_B Loading After (%) | 16.2
Minimum Voltage (V) | 210.7