## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 4 | 10 | 19 | 49.3 | 5.85 | 50 | 22.2 | 40.8 | 15.5 | 43 | 223.7 | 206.3 | 206.3 | NO
1 | OK | 5 | 28 | 48 | 61 | 0.4 | 11.87 | 50 | 22.2 | 40.8 | 8.4 | 46.6 | 228.5 | 210.1 | 210.1 | YES
| NG | 4 | 1 | 10 | 19 | 49.3 | 3.2 | 50 | 22.2 | 40.8 | 16.5 | 41.9 | 223.6 | 207.8 | 207.8 | NO
2 | OK | 4 | 21 | 20 | 19 | 60.6 | 0.93 | 50 | 22.2 | 40.8 | 21.1 | 41.2 | 223.4 | 210.1 | 210.1 | YES
3 | OK | 28 | 11 | 48 | 61 | 0.4 | 11.65 | 50 | 22.2 | 40.8 | 8.6 | 46.5 | 228.5 | 210.1 | 210.1 | YES
| NG | 1 | 0 | 10 | 19 | 49.3 | 3.2 | 50 | 22.2 | 40.8 | 18.5 | 41.9 | 223.5 | 207.8 | 207.8 | NO
4 | OK | 21 | 20 | 20 | 19 | 60.6 | 0.46 | 50 | 22.2 | 40.8 | 21.7 | 41 | 223.3 | 210.1 | 210.1 | YES
5 | OK | 11 | 31 | 6 | 13 | 81.2 | 0.84 | 50 | 22.2 | 40.8 | 21.2 | 41.2 | 223.3 | 210.1 | 210.1 | YES
6 | OK | 11 | 26 | 48 | 61 | 0.4 | 10.26 | 50 | 22.2 | 40.8 | 10.2 | 45.8 | 228.5 | 210.1 | 210.1 | YES
| NG | 0 | 7 | 10 | 19 | 49.3 | 3.2 | 50 | 22.2 | 40.8 | 18.5 | 41.9 | 223.5 | 207.8 | 207.8 | NO
7 | OK | 31 | 6 | 6 | 13 | 81.2 | 0.59 | 50 | 22.2 | 40.8 | 21.5 | 41.1 | 223.3 | 210.1 | 210.1 | YES
8 | OK | 26 | 27 | 48 | 61 | 0.4 | 10.26 | 50 | 22.2 | 40.8 | 10.2 | 45.8 | 228.5 | 210.1 | 210.1 | YES
| NG | 7 | 8 | 33 | 19 | 65.4 | 2.66 | 50 | 22.2 | 40.8 | 19.1 | 41.8 | 223.5 | 208.1 | 208.1 | NO
9 | OK | 7 | 9 | 10 | 19 | 49.3 | 0.54 | 50 | 22.2 | 40.8 | 21.6 | 40.9 | 223.4 | 210.1 | 210.1 | YES
10 | OK | 27 | 39 | 48 | 61 | 0.4 | 10.12 | 50 | 22.2 | 40.8 | 10.4 | 45.7 | 228.5 | 210.1 | 210.1 | YES
11 | OK | 8 | 32 | 33 | 19 | 65.4 | 1.44 | 50 | 22.2 | 40.8 | 20.5 | 41.3 | 223.4 | 210 | 210 | YES
12 | OK | 9 | 10 | 10 | 19 | 49.3 | 0.25 | 50 | 22.2 | 40.8 | 21.9 | 40.8 | 223.4 | 210.1 | 210.1 | YES
13 | OK | 39 | 40 | 48 | 61 | 0.4 | 10.12 | 50 | 22.2 | 40.8 | 10.4 | 45.7 | 228.5 | 210.1 | 210.1 | YES
14 | OK | 32 | 33 | 33 | 19 | 65.4 | 0.37 | 50 | 22.2 | 40.8 | 21.8 | 40.8 | 223.4 | 210.1 | 210.1 | YES
15 | OK | 32 | 34 | 34 | 19 | 97.7 | 1.07 | 50 | 22.2 | 40.8 | 21 | 41.3 | 223.3 | 210 | 210 | YES
16 | OK | 40 | 46 | 48 | 61 | 0.4 | 10.12 | 50 | 22.2 | 40.8 | 10.4 | 45.7 | 228.5 | 210.1 | 210.1 | YES
17 | OK | 46 | 41 | 48 | 61 | 0.4 | 10.12 | 50 | 22.2 | 40.8 | 10.4 | 45.7 | 228.5 | 210.1 | 210.1 | YES
18 | OK | 41 | 45 | 48 | 61 | 0.4 | 2.41 | 50 | 22.2 | 40.8 | 19.4 | 41.9 | 223.5 | 210.1 | 210.1 | YES
19 | OK | 45 | 43 | 48 | 61 | 0.4 | 2.41 | 50 | 22.2 | 40.8 | 19.4 | 41.9 | 223.5 | 210.1 | 210.1 | YES
20 | OK | 43 | 13 | 48 | 61 | 0.4 | 2.11 | 50 | 22.2 | 40.8 | 19.8 | 41.7 | 223.5 | 210.1 | 210.1 | YES
21 | OK | 13 | 14 | 48 | 61 | 0.4 | 2.11 | 50 | 22.2 | 40.8 | 19.8 | 41.7 | 223.5 | 210.1 | 210.1 | YES
22 | OK | 14 | 44 | 48 | 61 | 0.4 | 1.69 | 50 | 22.2 | 40.8 | 20.2 | 41.5 | 223.5 | 210.1 | 210.1 | YES
23 | OK | 44 | 15 | 48 | 61 | 0.4 | 1.69 | 50 | 22.2 | 40.8 | 20.2 | 41.5 | 223.5 | 210.1 | 210.1 | YES
24 | OK | 15 | 16 | 48 | 61 | 0.4 | 1.48 | 50 | 22.2 | 40.8 | 20.5 | 41.4 | 223.5 | 210.1 | 210.1 | YES
25 | OK | 16 | 17 | 48 | 61 | 0.4 | 1.24 | 50 | 22.2 | 40.8 | 20.7 | 41.3 | 223.5 | 210.1 | 210.1 | YES
26 | ** OPTIMAL ** | 17 | 18 | 48 | 61 | 0.4 | 0.36 | 50 | 22.2 | 40.8 | 21.8 | 40.9 | 223.6 | 210.1 | 210.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-032379
TR_B (available) | 55-009940
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 22.2
TR_B Baseline Loading% | 40.8
Total Scenarios Evaluated | 31
Feasible Scenarios | 26
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 18
Tie Node (TR_A side) | 48
Tie Node (TR_B side) | 61
Tie Line Distance (m) | 0.4
Load Transferred (kW) | 0.36
TR_A Loading After (%) | 21.8
TR_B Loading After (%) | 40.9
Minimum Voltage (V) | 210.1