## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 5 | 4 | 24 | 24 | 14 | 5.85 | 50 | 22.2 | 14.5 | 15.5 | 16.4 | 223.7 | 223.9 | 223.7 | YES
2 | OK | 4 | 1 | 24 | 24 | 14 | 3.2 | 50 | 22.2 | 14.5 | 16.5 | 15.9 | 223.6 | 225.5 | 223.6 | YES
3 | OK | 1 | 0 | 24 | 24 | 14 | 3.2 | 50 | 22.2 | 14.5 | 18.5 | 15.9 | 223.5 | 225.5 | 223.5 | YES
4 | OK | 0 | 7 | 24 | 24 | 14 | 3.2 | 50 | 22.2 | 14.5 | 18.5 | 15.9 | 223.5 | 225.5 | 223.5 | YES
5 | OK | 7 | 8 | 24 | 24 | 14 | 2.66 | 50 | 22.2 | 14.5 | 19.1 | 15.9 | 223.5 | 225.5 | 223.5 | YES
6 | OK | 8 | 32 | 24 | 24 | 14 | 1.44 | 50 | 22.2 | 14.5 | 20.5 | 15.3 | 223.4 | 226.8 | 223.4 | YES
7 | OK | 32 | 34 | 24 | 24 | 14 | 1.07 | 50 | 22.2 | 14.5 | 21 | 15.3 | 223.3 | 226.8 | 223.3 | YES
8 | OK | 34 | 42 | 24 | 24 | 14 | 1.07 | 50 | 22.2 | 14.5 | 21 | 15.3 | 223.3 | 226.8 | 223.3 | YES
9 | OK | 42 | 38 | 24 | 24 | 14 | 0.55 | 50 | 22.2 | 14.5 | 21.5 | 14.9 | 223.3 | 227 | 223.3 | YES
10 | OK | 38 | 36 | 24 | 24 | 14 | 0.55 | 50 | 22.2 | 14.5 | 21.5 | 14.9 | 223.3 | 227 | 223.3 | YES
11 | OK | 36 | 35 | 24 | 24 | 14 | 0.55 | 50 | 22.2 | 14.5 | 21.5 | 14.9 | 223.3 | 227 | 223.3 | YES
12 | OK | 35 | 37 | 24 | 24 | 14 | 0.55 | 50 | 22.2 | 14.5 | 21.5 | 14.9 | 223.3 | 227 | 223.3 | YES
13 | OK | 37 | 29 | 24 | 24 | 14 | 0.51 | 50 | 22.2 | 14.5 | 21.6 | 14.9 | 223.3 | 227 | 223.3 | YES
14 | OK | 29 | 30 | 24 | 24 | 14 | 0.51 | 50 | 22.2 | 14.5 | 21.6 | 14.9 | 223.3 | 227 | 223.3 | YES
15 | OK | 30 | 3 | 24 | 24 | 14 | 0.51 | 50 | 22.2 | 14.5 | 21.6 | 14.9 | 223.3 | 227 | 223.3 | YES
16 | OK | 3 | 2 | 24 | 24 | 14 | 0.49 | 50 | 22.2 | 14.5 | 21.6 | 14.9 | 223.3 | 227 | 223.3 | YES
17 | OK | 2 | 24 | 24 | 24 | 14 | 0.49 | 50 | 22.2 | 14.5 | 21.6 | 14.9 | 223.3 | 227 | 223.3 | YES
18 | OK | 24 | 23 | 23 | 6 | 14.6 | 0.15 | 50 | 22.2 | 14.5 | 22 | 14.6 | 223.3 | 227.1 | 223.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-032379
TR_B (available) | 68-011558
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 22.2
TR_B Baseline Loading% | 14.5
Total Scenarios Evaluated | 18
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 4
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 24
Tie Line Distance (m) | 14
Load Transferred (kW) | 5.85
TR_A Loading After (%) | 15.5
TR_B Loading After (%) | 16.4
Minimum Voltage (V) | 223.7