## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 8 | 7 | 37 | 11 | 48.2 | 5.4 | 50 | 61.9 | 29.3 | 49.4 | 42 | 216.2 | 219.7 | 216.2 | YES
| NG | 8 | 24 | 72 | 17 | 45.1 | 21.13 | 50 | 61.9 | 29.3 | 12.4 | 53.5 | 227.3 | 205.2 | 205.2 | NO
2 | OK | 7 | 21 | 37 | 11 | 48.2 | 5.4 | 50 | 61.9 | 29.3 | 49.4 | 42 | 216.2 | 219.7 | 216.2 | YES
| NG | 24 | 25 | 72 | 17 | 45.1 | 21.13 | 50 | 61.9 | 29.3 | 12.4 | 53.5 | 227.3 | 205.2 | 205.2 | NO
| NG | 25 | 5 | 72 | 17 | 45.1 | 19.35 | 50 | 61.9 | 29.3 | 16.5 | 49.6 | 227.1 | 208.9 | 208.9 | NO
| NG | 5 | 6 | 72 | 17 | 45.1 | 17.49 | 50 | 61.9 | 29.3 | 20.8 | 49.6 | 226.5 | 208.9 | 208.9 | NO
| NG | 6 | 26 | 72 | 17 | 45.1 | 17.49 | 50 | 61.9 | 29.3 | 20.8 | 49.6 | 226.5 | 208.9 | 208.9 | NO
| NG | 26 | 4 | 72 | 17 | 45.1 | 16.85 | 50 | 61.9 | 29.3 | 22.2 | 49.6 | 226.2 | 208.9 | 208.9 | NO
3 | OK | 4 | 2 | 72 | 17 | 45.1 | 13.38 | 50 | 61.9 | 29.3 | 30 | 41.1 | 225 | 216.8 | 216.8 | YES
4 | OK | 2 | 0 | 72 | 17 | 45.1 | 13.38 | 50 | 61.9 | 29.3 | 30.3 | 41.1 | 225 | 216.8 | 216.8 | YES
5 | OK | 0 | 1 | 72 | 17 | 45.1 | 12.63 | 50 | 61.9 | 29.3 | 32 | 41.1 | 225.1 | 216.8 | 216.8 | YES
6 | OK | 1 | 9 | 72 | 17 | 45.1 | 6.58 | 50 | 61.9 | 29.3 | 46.2 | 34.4 | 218.2 | 224.7 | 218.2 | YES
7 | ** OPTIMAL ** | 9 | 10 | 72 | 17 | 45.1 | 6.58 | 50 | 61.9 | 29.3 | 46.2 | 34.4 | 218.2 | 224.7 | 218.2 | YES
8 | OK | 10 | 39 | 72 | 17 | 45.1 | 6.44 | 50 | 61.9 | 29.3 | 46.5 | 34 | 217.9 | 225 | 217.9 | YES
9 | OK | 39 | 41 | 72 | 17 | 45.1 | 4.68 | 50 | 61.9 | 29.3 | 50.7 | 31.4 | 216.2 | 226 | 216.2 | YES
10 | OK | 41 | 45 | 72 | 17 | 45.1 | 0.9 | 50 | 61.9 | 29.3 | 59.7 | 31.4 | 216.9 | 226 | 216.9 | YES
11 | OK | 45 | 46 | 72 | 17 | 45.1 | 0.9 | 50 | 61.9 | 29.3 | 59.7 | 30.8 | 216.9 | 226 | 216.9 | YES
12 | OK | 46 | 47 | 72 | 17 | 45.1 | 0.67 | 50 | 61.9 | 29.3 | 60.2 | 30.8 | 216.5 | 226 | 216.5 | YES
13 | OK | 47 | 71 | 72 | 17 | 45.1 | 0.67 | 50 | 61.9 | 29.3 | 60.2 | 30.8 | 216.5 | 226 | 216.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-034715
TR_B (available) | 54-004339
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 61.9
TR_B Baseline Loading% | 29.3
Total Scenarios Evaluated | 19
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 10
Tie Node (TR_A side) | 72
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 45.1
Load Transferred (kW) | 6.58
TR_A Loading After (%) | 46.2
TR_B Loading After (%) | 34.4
Minimum Voltage (V) | 218.2