## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 8 | 7 | 53 | 56 | 31.8 | 5.4 | 50 | 61.9 | 21.5 | 49.4 | 23.4 | 216.2 | 223.5 | 216.2 | YES
2 | OK | 7 | 21 | 53 | 56 | 31.8 | 5.4 | 50 | 61.9 | 21.5 | 49.4 | 23.4 | 216.2 | 223.5 | 216.2 | YES
3 | OK | 21 | 23 | 53 | 56 | 31.8 | 5.4 | 50 | 61.9 | 21.5 | 49.4 | 23.4 | 216.2 | 223.5 | 216.2 | YES
4 | ** OPTIMAL ** | 23 | 66 | 53 | 56 | 31.8 | 4.99 | 50 | 61.9 | 21.5 | 50.4 | 23.4 | 216.2 | 223.5 | 216.2 | YES
5 | OK | 66 | 28 | 53 | 56 | 31.8 | 4.58 | 50 | 61.9 | 21.5 | 51.3 | 22.9 | 216 | 223.5 | 216 | YES
6 | OK | 28 | 29 | 29 | 56 | 147.7 | 2.62 | 50 | 61.9 | 21.5 | 55.8 | 22.1 | 215.6 | 223.5 | 215.6 | YES
7 | OK | 28 | 58 | 53 | 56 | 31.8 | 1.96 | 50 | 61.9 | 21.5 | 57.3 | 22.3 | 215.7 | 223.5 | 215.7 | YES
8 | OK | 58 | 59 | 53 | 56 | 31.8 | 1.84 | 50 | 61.9 | 21.5 | 57.6 | 22.2 | 215.7 | 223.5 | 215.7 | YES
9 | OK | 59 | 30 | 53 | 56 | 31.8 | 1.84 | 50 | 61.9 | 21.5 | 57.6 | 22.2 | 215.7 | 223.5 | 215.7 | YES
10 | OK | 30 | 31 | 53 | 56 | 31.8 | 1.78 | 50 | 61.9 | 21.5 | 57.8 | 22.1 | 215.6 | 223.5 | 215.6 | YES
11 | OK | 31 | 53 | 53 | 56 | 31.8 | 1.39 | 50 | 61.9 | 21.5 | 58.7 | 22.1 | 215.6 | 223.5 | 215.6 | YES
12 | OK | 53 | 34 | 34 | 55 | 34.3 | 1.39 | 50 | 61.9 | 21.5 | 58.7 | 22.1 | 215.6 | 223.5 | 215.6 | YES
13 | OK | 34 | 32 | 32 | 55 | 42.9 | 1.39 | 50 | 61.9 | 21.5 | 58.7 | 22.1 | 215.6 | 223.5 | 215.6 | YES
14 | OK | 32 | 33 | 33 | 55 | 64.6 | 0.81 | 50 | 61.9 | 21.5 | 58.7 | 21.5 | 215.6 | 223.5 | 215.6 | YES
15 | OK | 32 | 35 | 35 | 55 | 45.3 | 0.58 | 50 | 61.9 | 21.5 | 60.5 | 21.5 | 215.6 | 223.5 | 215.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-034715
TR_B (available) | 60-025358
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 61.9
TR_B Baseline Loading% | 21.5
Total Scenarios Evaluated | 15
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 66
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 56
Tie Line Distance (m) | 31.8
Load Transferred (kW) | 4.99
TR_A Loading After (%) | 50.4
TR_B Loading After (%) | 23.4
Minimum Voltage (V) | 216.2