## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 7 | 38 | 46 | 45.2 | 5.4 | 50 | 61.9 | 47.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 8 | 24 | 24 | 46 | 96 | 21.13 | 50 | 61.9 | 47.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 7 | 21 | 38 | 46 | 45.2 | 5.4 | 50 | 61.9 | 47.8 | 49.4 | 54.3 | 216.2 | 216.8 | 216.2 | YES
| NG | 24 | 25 | 25 | 46 | 130.4 | 21.13 | 50 | 61.9 | 47.8 | 12.4 | 75 | 227.3 | 190.9 | 190.9 | NO
2 | OK | 21 | 23 | 23 | 53 | 76.7 | 5.4 | 50 | 61.9 | 47.8 | 49.4 | 54.2 | 216.2 | 216.8 | 216.2 | YES
3 | ** OPTIMAL ** | 23 | 66 | 66 | 53 | 92.3 | 4.99 | 50 | 61.9 | 47.8 | 50.4 | 53.8 | 216.2 | 216.8 | 216.2 | YES
4 | OK | 66 | 28 | 52 | 53 | 93.3 | 4.58 | 50 | 61.9 | 47.8 | 51.3 | 53.3 | 216 | 217.1 | 216 | YES
5 | OK | 28 | 29 | 52 | 53 | 93.3 | 2.62 | 50 | 61.9 | 47.8 | 55.8 | 50.9 | 215.6 | 217.6 | 215.6 | YES
6 | OK | 28 | 58 | 58 | 53 | 103.5 | 1.96 | 50 | 61.9 | 47.8 | 57.3 | 50.2 | 215.7 | 217.4 | 215.7 | YES
| NG | 29 | 50 | 52 | 53 | 93.3 | 1.31 | 50 | 61.9 | 47.8 | 57.6 | 121.2 | 215.6 | 7.3 | 7.3 | NO
7 | OK | 58 | 59 | 59 | 52 | 129.7 | 1.84 | 50 | 61.9 | 47.8 | 57.6 | 50 | 215.7 | 217.5 | 215.7 | YES
8 | OK | 50 | 51 | 52 | 53 | 93.3 | 1.02 | 50 | 61.9 | 47.8 | 59.5 | 48.4 | 215.6 | 217.4 | 215.6 | YES
9 | OK | 59 | 30 | 30 | 52 | 140.4 | 1.84 | 50 | 61.9 | 47.8 | 57.6 | 50 | 215.7 | 217.5 | 215.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-034715
TR_B (available) | 60-036522
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 61.9
TR_B Baseline Loading% | 47.8
Total Scenarios Evaluated | 13
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 66
Tie Node (TR_A side) | 66
Tie Node (TR_B side) | 53
Tie Line Distance (m) | 92.3
Load Transferred (kW) | 4.99
TR_A Loading After (%) | 50.4
TR_B Loading After (%) | 53.8
Minimum Voltage (V) | 216.2