## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 7 | 48 | 0 | 41.1 | 5.4 | 50 | 61.9 | 2.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 7 | 21 | 48 | 0 | 41.1 | 5.4 | 50 | 61.9 | 2.9 | 49.4 | 6.8 | 216.2 | 227.2 | 216.2 | YES
2 | OK | 21 | 23 | 48 | 0 | 41.1 | 5.4 | 50 | 61.9 | 2.9 | 49.4 | 6.8 | 216.2 | 227.2 | 216.2 | YES
3 | ** OPTIMAL ** | 23 | 66 | 48 | 0 | 41.1 | 4.99 | 50 | 61.9 | 2.9 | 50.4 | 6.5 | 216.2 | 228 | 216.2 | YES
4 | OK | 66 | 28 | 48 | 0 | 41.1 | 4.58 | 50 | 61.9 | 2.9 | 51.3 | 6.2 | 216 | 227.8 | 216 | YES
5 | OK | 28 | 58 | 48 | 0 | 41.1 | 1.96 | 50 | 61.9 | 2.9 | 57.3 | 4.3 | 215.7 | 229.6 | 215.7 | YES
6 | OK | 58 | 59 | 48 | 0 | 41.1 | 1.84 | 50 | 61.9 | 2.9 | 57.6 | 4.2 | 215.7 | 229.6 | 215.7 | YES
7 | OK | 59 | 30 | 48 | 0 | 41.1 | 1.84 | 50 | 61.9 | 2.9 | 57.6 | 4.2 | 215.7 | 229.6 | 215.7 | YES
8 | OK | 30 | 31 | 48 | 0 | 41.1 | 1.78 | 50 | 61.9 | 2.9 | 57.8 | 4.2 | 215.6 | 229.6 | 215.6 | YES
9 | OK | 31 | 53 | 48 | 0 | 41.1 | 1.39 | 50 | 61.9 | 2.9 | 58.7 | 3.9 | 215.6 | 230.1 | 215.6 | YES
10 | OK | 53 | 34 | 48 | 0 | 41.1 | 1.39 | 50 | 61.9 | 2.9 | 58.7 | 3.9 | 215.6 | 230.1 | 215.6 | YES
11 | OK | 34 | 32 | 48 | 0 | 41.1 | 1.39 | 50 | 61.9 | 2.9 | 58.7 | 3.9 | 215.6 | 230.1 | 215.6 | YES
12 | OK | 32 | 33 | 48 | 0 | 41.1 | 0.81 | 50 | 61.9 | 2.9 | 58.7 | 3.5 | 215.6 | 230 | 215.6 | YES
13 | OK | 32 | 35 | 60 | 0 | 75.5 | 0.58 | 50 | 61.9 | 2.9 | 60.5 | 2.9 | 215.6 | 230.1 | 215.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-034715
TR_B (available) | 61-015212
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 61.9
TR_B Baseline Loading% | 2.9
Total Scenarios Evaluated | 14
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 66
Tie Node (TR_A side) | 48
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 41.1
Load Transferred (kW) | 4.99
TR_A Loading After (%) | 50.4
TR_B Loading After (%) | 6.5
Minimum Voltage (V) | 216.2