## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 49 | 15 | 65 | 53.2 | 50.73 | 50 | 79.7 | 44.6 | 19.1 | 58.8 | 226.8 | 158.3 | 158.3 | NO
| NG | 50 | 47 | 64 | 65 | 31.6 | 16.56 | 50 | 79.7 | 44.6 | 60.6 | 47.7 | 206.4 | 211.7 | 206.4 | NO
| NG | 49 | 46 | 15 | 65 | 53.2 | 45.73 | 50 | 79.7 | 44.6 | 24.8 | 58.6 | 226.8 | 159.3 | 159.3 | NO
| NG | 47 | 51 | 64 | 65 | 31.6 | 13.38 | 50 | 79.7 | 44.6 | 64.3 | 47.1 | 206.1 | 211.7 | 206.1 | NO
| NG | 46 | 45 | 15 | 65 | 53.2 | 45.73 | 50 | 79.7 | 44.6 | 24.8 | 58.6 | 226.8 | 159.3 | 159.3 | NO
| NG | 51 | 3 | 64 | 65 | 31.6 | 13.29 | 50 | 79.7 | 44.6 | 64.4 | 47.1 | 206.1 | 211.7 | 206.1 | NO
| NG | 45 | 44 | 15 | 65 | 53.2 | 43.94 | 50 | 79.7 | 44.6 | 26.8 | 57.5 | 226.6 | 165.6 | 165.6 | NO
| NG | 3 | 19 | 64 | 65 | 31.6 | 13.29 | 50 | 79.7 | 44.6 | 64.4 | 47.1 | 206.1 | 211.7 | 206.1 | NO
| NG | 44 | 21 | 15 | 65 | 53.2 | 37.95 | 50 | 79.7 | 44.6 | 33.7 | 55.5 | 226.1 | 176.5 | 176.5 | NO
| NG | 19 | 20 | 64 | 65 | 31.6 | 11.03 | 50 | 79.7 | 44.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 44.6% (degenerate)
| NG | 19 | 0 | 2 | 16 | 63.3 | 1.34 | 50 | 79.7 | 44.6 | 78.2 | 45.2 | 205.1 | 211.7 | 205.1 | NO
| NG | 21 | 22 | 15 | 65 | 53.2 | 37.95 | 50 | 79.7 | 44.6 | 33.7 | 55.5 | 226.1 | 176.5 | 176.5 | NO
| NG | 20 | 29 | 64 | 65 | 31.6 | 8.76 | 50 | 79.7 | 44.6 | 69.4 | 45.6 | 205.4 | 211.7 | 205.4 | NO
| NG | 20 | 58 | 28 | 64 | 56.5 | 2.12 | 50 | 79.7 | 44.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 44.6% (degenerate)
| NG | 0 | 1 | 2 | 16 | 63.3 | 0.71 | 50 | 79.7 | 44.6 | 78.9 | 84.1 | 204.9 | 9.4 | 9.4 | NO
| NG | 22 | 32 | 15 | 65 | 53.2 | 37.44 | 50 | 79.7 | 44.6 | 34.3 | 55.1 | 226 | 178.6 | 178.6 | NO
| NG | 29 | 17 | 64 | 65 | 31.6 | 6.47 | 50 | 79.7 | 44.6 | 72.2 | 45.6 | 205.4 | 211.7 | 205.4 | NO
| NG | 58 | 59 | 59 | 65 | 102.8 | 0.45 | 50 | 79.7 | 44.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 44.6% (degenerate)
| NG | 58 | 30 | 28 | 64 | 56.5 | 1.67 | 50 | 79.7 | 44.6 | 77.8 | 45.3 | 205.3 | 211.7 | 205.3 | NO
| NG | 1 | 2 | 2 | 16 | 63.3 | 0.53 | 50 | 79.7 | 44.6 | 79.1 | 44.8 | 204.9 | 211.7 | 204.9 | NO
| NG | 32 | 33 | 15 | 65 | 53.2 | 36.62 | 50 | 79.7 | 44.6 | 35.2 | 54.5 | 225.8 | 181.6 | 181.6 | NO
| NG | 17 | 18 | 18 | 65 | 56.8 | 2.66 | 50 | 79.7 | 44.6 | 76.6 | 45.9 | 205 | 211.7 | 205 | NO
| NG | 17 | 63 | 64 | 65 | 31.6 | 1.76 | 50 | 79.7 | 44.6 | 77.7 | 45.4 | 205.3 | 211.7 | 205.3 | NO
| NG | 30 | 28 | 28 | 64 | 56.5 | 1.57 | 50 | 79.7 | 44.6 | 77.9 | 45.3 | 205.2 | 211.7 | 205.2 | NO
| NG | 33 | 62 | 15 | 65 | 53.2 | 36.52 | 50 | 79.7 | 44.6 | 35.4 | 54.5 | 225.8 | 181.6 | 181.6 | NO
| NG | 18 | 24 | 26 | 65 | 58.3 | 1.02 | 50 | 79.7 | 44.6 | 78.6 | 45 | 205 | 211.7 | 205 | NO
| NG | 63 | 64 | 64 | 65 | 31.6 | 1.35 | 50 | 79.7 | 44.6 | 78.2 | 45.2 | 205.2 | 211.7 | 205.2 | NO
| NG | 62 | 10 | 15 | 65 | 53.2 | 36.27 | 50 | 79.7 | 44.6 | 35.6 | 54.5 | 225.8 | 181.6 | 181.6 | NO
| NG | 24 | 25 | 26 | 65 | 58.3 | 0.52 | 50 | 79.7 | 44.6 | 79.1 | 44.8 | 205 | 211.7 | 205 | NO
| NG | 24 | 27 | 27 | 65 | 68.3 | 0.5 | 50 | 79.7 | 44.6 | 79.2 | 44.8 | 204.8 | 211.7 | 204.8 | NO
| NG | 10 | 9 | 15 | 65 | 53.2 | 28.22 | 50 | 79.7 | 44.6 | 45 | 53.4 | 224.3 | 186.8 | 186.8 | NO
| NG | 10 | 31 | 31 | 65 | 136.5 | 7.53 | 50 | 79.7 | 44.6 | 70 | 48.3 | 205.7 | 210.6 | 205.7 | NO
| NG | 25 | 26 | 26 | 65 | 58.3 | 0.52 | 50 | 79.7 | 44.6 | 79.1 | 44.6 | 205 | 211.7 | 205 | NO
| NG | 27 | 68 | 68 | 65 | 70.2 | 0.5 | 50 | 79.7 | 44.6 | 79.2 | 44.8 | 204.8 | 211.7 | 204.8 | NO
| NG | 9 | 11 | 35 | 69 | 60.2 | 19.15 | 50 | 79.7 | 44.6 | 54.9 | 55.8 | 218.9 | 179.1 | 179.1 | NO
1 | ** OPTIMAL ** | 9 | 12 | 15 | 65 | 53.2 | 8.34 | 50 | 79.7 | 44.6 | 69 | 47.2 | 213 | 211.7 | 211.7 | YES
| NG | 11 | 8 | 35 | 69 | 60.2 | 13.33 | 50 | 79.7 | 44.6 | 57.6 | 51.8 | 218.3 | 195.6 | 195.6 | NO
| NG | 12 | 13 | 13 | 65 | 71.7 | 3.03 | 50 | 79.7 | 44.6 | 75.6 | 46 | 209.7 | 211.7 | 209.7 | NO
| NG | 12 | 14 | 15 | 65 | 53.2 | 5.31 | 50 | 79.7 | 44.6 | 73 | 45.7 | 208.3 | 211.7 | 208.3 | NO
| NG | 8 | 6 | 35 | 69 | 60.2 | 4.05 | 50 | 79.7 | 44.6 | 74.7 | 46.6 | 206.6 | 211.7 | 206.6 | NO
| NG | 14 | 16 | 15 | 65 | 53.2 | 2.49 | 50 | 79.7 | 44.6 | 76.4 | 45.7 | 208.9 | 211.7 | 208.9 | NO
| NG | 6 | 5 | 35 | 69 | 60.2 | 2.89 | 50 | 79.7 | 44.6 | 76.1 | 46 | 207.1 | 211.7 | 207.1 | NO
| NG | 16 | 23 | 15 | 65 | 53.2 | 2.49 | 50 | 79.7 | 44.6 | 76.4 | 45.7 | 208.9 | 211.7 | 208.9 | NO
| NG | 5 | 7 | 35 | 69 | 60.2 | 2.89 | 50 | 79.7 | 44.6 | 76.1 | 46 | 207.1 | 211.7 | 207.1 | NO
| NG | 23 | 15 | 15 | 65 | 53.2 | 1.31 | 50 | 79.7 | 44.6 | 77.9 | 45.2 | 207 | 211.7 | 207 | NO
| NG | 7 | 37 | 35 | 69 | 60.2 | 2.12 | 50 | 79.7 | 44.6 | 77.2 | 45.6 | 205.5 | 211.7 | 205.5 | NO
| NG | 37 | 36 | 35 | 69 | 60.2 | 0.68 | 50 | 79.7 | 44.6 | 78.9 | 44.9 | 205.6 | 211.7 | 205.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 67-035828
TR_B (available) | 66-017011
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 79.7
TR_B Baseline Loading% | 44.6
Total Scenarios Evaluated | 47
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 12
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 65
Tie Line Distance (m) | 53.2
Load Transferred (kW) | 8.34
TR_A Loading After (%) | 69
TR_B Loading After (%) | 47.2
Minimum Voltage (V) | 211.7