## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 49 | 41 | 35 | 1 | 50.73 | 95 | 79.7 | 22.5 | 19.1 | 60.9 | 226.8 | 205.5 | 205.5 | NO
| NG | 50 | 47 | 68 | 36 | 148.5 | 16.56 | 50 | 79.7 | 22.5 | 60.6 | 34.7 | 206.4 | 218.2 | 206.4 | NO
| NG | 49 | 46 | 41 | 35 | 1 | 45.73 | 95 | 79.7 | 22.5 | 24.8 | 57.1 | 226.8 | 205.2 | 205.2 | NO
| NG | 47 | 51 | 68 | 36 | 148.5 | 13.38 | 50 | 79.7 | 22.5 | 64.3 | 32.3 | 206.1 | 219.8 | 206.1 | NO
| NG | 46 | 45 | 41 | 35 | 1 | 45.73 | 95 | 79.7 | 22.5 | 24.8 | 57.1 | 226.8 | 205.2 | 205.2 | NO
| NG | 51 | 3 | 68 | 36 | 148.5 | 13.29 | 50 | 79.7 | 22.5 | 64.4 | 32.3 | 206.1 | 219.8 | 206.1 | NO
| NG | 45 | 44 | 41 | 35 | 1 | 43.94 | 95 | 79.7 | 22.5 | 26.8 | 55.5 | 226.6 | 206.1 | 206.1 | NO
| NG | 3 | 19 | 68 | 36 | 148.5 | 13.29 | 50 | 79.7 | 22.5 | 64.4 | 32.3 | 206.1 | 219.8 | 206.1 | NO
| NG | 44 | 21 | 41 | 35 | 1 | 37.95 | 95 | 79.7 | 22.5 | 33.7 | 51 | 226.1 | 208.1 | 208.1 | NO
| NG | 19 | 20 | 68 | 36 | 148.5 | 11.03 | 50 | 79.7 | 22.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 22.5% (degenerate)
| NG | 21 | 22 | 41 | 35 | 1 | 37.95 | 95 | 79.7 | 22.5 | 33.7 | 51 | 226.1 | 208.1 | 208.1 | NO
| NG | 20 | 29 | 68 | 36 | 148.5 | 8.76 | 50 | 79.7 | 22.5 | 69.4 | 28.9 | 205.4 | 223.6 | 205.4 | NO
| NG | 22 | 32 | 41 | 35 | 1 | 37.44 | 95 | 79.7 | 22.5 | 34.3 | 50.6 | 226 | 208.7 | 208.7 | NO
| NG | 29 | 17 | 68 | 36 | 148.5 | 6.47 | 50 | 79.7 | 22.5 | 72.2 | 27.2 | 205.4 | 223.6 | 205.4 | NO
| NG | 32 | 33 | 41 | 35 | 1 | 36.62 | 95 | 79.7 | 22.5 | 35.2 | 49.9 | 225.8 | 209.5 | 209.5 | NO
| NG | 17 | 18 | 68 | 36 | 148.5 | 2.66 | 50 | 79.7 | 22.5 | 76.6 | 24.5 | 205 | 223.8 | 205 | NO
| NG | 33 | 62 | 41 | 35 | 1 | 36.52 | 95 | 79.7 | 22.5 | 35.4 | 49.8 | 225.8 | 209.5 | 209.5 | NO
| NG | 18 | 24 | 68 | 36 | 148.5 | 1.02 | 50 | 79.7 | 22.5 | 78.6 | 23.3 | 205 | 223.8 | 205 | NO
| NG | 62 | 10 | 41 | 35 | 1 | 36.27 | 95 | 79.7 | 22.5 | 35.6 | 49.7 | 225.8 | 209.4 | 209.4 | NO
| NG | 24 | 27 | 68 | 36 | 148.5 | 0.5 | 50 | 79.7 | 22.5 | 79.2 | 22.9 | 204.8 | 223.9 | 204.8 | NO
1 | OK | 10 | 9 | 5 | 36 | 40.3 | 28.22 | 50 | 79.7 | 22.5 | 45 | 43.6 | 224.3 | 211.3 | 211.3 | YES
| NG | 10 | 31 | 41 | 35 | 1 | 7.53 | 95 | 79.7 | 22.5 | 70 | 28 | 205.7 | 223.8 | 205.7 | NO
| NG | 27 | 68 | 68 | 36 | 148.5 | 0.5 | 50 | 79.7 | 22.5 | 79.2 | 22.9 | 204.8 | 223.9 | 204.8 | NO
2 | ** OPTIMAL ** | 9 | 11 | 5 | 36 | 40.3 | 19.15 | 50 | 79.7 | 22.5 | 54.9 | 36.6 | 218.9 | 218.6 | 218.6 | YES
3 | OK | 9 | 12 | 12 | 36 | 117.3 | 8.34 | 50 | 79.7 | 22.5 | 69 | 28.6 | 213 | 221.1 | 213 | YES
| NG | 31 | 34 | 41 | 35 | 1 | 7.13 | 95 | 79.7 | 22.5 | 71.1 | 27.7 | 204.9 | 223.8 | 204.9 | NO
4 | OK | 11 | 8 | 5 | 36 | 40.3 | 13.33 | 50 | 79.7 | 22.5 | 57.6 | 32.3 | 218.3 | 218.6 | 218.3 | YES
| NG | 12 | 13 | 13 | 36 | 131.4 | 3.03 | 50 | 79.7 | 22.5 | 75.6 | 24.7 | 209.7 | 223.5 | 209.7 | NO
| NG | 12 | 14 | 14 | 36 | 121.3 | 5.31 | 50 | 79.7 | 22.5 | 73 | 26.4 | 208.3 | 223.6 | 208.3 | NO
| NG | 34 | 42 | 41 | 35 | 1 | 5.13 | 95 | 79.7 | 22.5 | 73.5 | 26.2 | 205.3 | 223.8 | 205.3 | NO
| NG | 8 | 6 | 5 | 36 | 40.3 | 4.05 | 50 | 79.7 | 22.5 | 74.7 | 25.5 | 206.6 | 223.7 | 206.6 | NO
| NG | 14 | 16 | 16 | 36 | 143.5 | 2.49 | 50 | 79.7 | 22.5 | 76.4 | 24.4 | 208.9 | 223.5 | 208.9 | NO
| NG | 42 | 43 | 41 | 35 | 1 | 3.67 | 95 | 79.7 | 22.5 | 75.2 | 25.2 | 205.8 | 223.8 | 205.8 | NO
| NG | 6 | 5 | 5 | 36 | 40.3 | 2.89 | 50 | 79.7 | 22.5 | 76.1 | 24.6 | 207.1 | 223.7 | 207.1 | NO
| NG | 16 | 23 | 23 | 36 | 144.9 | 2.49 | 50 | 79.7 | 22.5 | 76.4 | 24.3 | 208.9 | 223.6 | 208.9 | NO
| NG | 43 | 40 | 41 | 35 | 1 | 2.8 | 95 | 79.7 | 22.5 | 76.4 | 24.6 | 204.6 | 223.9 | 204.6 | NO
| NG | 5 | 7 | 7 | 36 | 116.1 | 2.89 | 50 | 79.7 | 22.5 | 76.1 | 24.6 | 207.1 | 223.7 | 207.1 | NO
| NG | 23 | 15 | 15 | 36 | 150 | 1.31 | 50 | 79.7 | 22.5 | 77.9 | 23.5 | 207 | 223.7 | 207 | NO
| NG | 40 | 41 | 41 | 35 | 1 | 2.8 | 95 | 79.7 | 22.5 | 76.4 | 24.6 | 204.6 | 223.9 | 204.6 | NO
| NG | 7 | 37 | 37 | 30 | 140.1 | 2.12 | 50 | 79.7 | 22.5 | 77.2 | 24.1 | 205.5 | 223.8 | 205.5 | NO
| NG | 41 | 39 | 39 | 39 | 1 | 2.8 | 95 | 79.7 | 22.5 | 76.4 | 24.5 | 204.6 | 223.9 | 204.6 | NO
| NG | 37 | 36 | 36 | 30 | 141.6 | 0.68 | 50 | 79.7 | 22.5 | 78.9 | 23 | 205.6 | 223.8 | 205.6 | NO
| NG | 39 | 38 | 38 | 21 | 1.7 | 0.76 | 95 | 79.7 | 22.5 | 78.8 | 23.1 | 204.6 | 223.9 | 204.6 | NO
| NG | 38 | 66 | 66 | 21 | 5.1 | 0.76 | 95 | 79.7 | 22.5 | 78.8 | 23.1 | 204.6 | 223.9 | 204.6 | NO
| NG | 66 | 65 | 65 | 11 | 14.4 | 0.76 | 50 | 79.7 | 22.5 | 78.8 | 22.6 | 204.6 | 223.9 | 204.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 67-035828
TR_B (available) | 66-018301
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 79.7
TR_B Baseline Loading% | 22.5
Total Scenarios Evaluated | 45
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 11
Tie Node (TR_A side) | 5
Tie Node (TR_B side) | 36
Tie Line Distance (m) | 40.3
Load Transferred (kW) | 19.15
TR_A Loading After (%) | 54.9
TR_B Loading After (%) | 36.6
Minimum Voltage (V) | 218.6