## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 49 | 46 | 20 | 26.3 | 50.73 | 95 | 79.7 | 10.4 | 19.1 | 35 | 226.8 | 205.1 | 205.1 | NO
| NG | 50 | 47 | 48 | 20 | 42.8 | 16.56 | 95 | 79.7 | 10.4 | 60.6 | 18.1 | 206.4 | 225.2 | 206.4 | NO
| NG | 49 | 56 | 56 | 20 | 34.7 | 1.62 | 95 | 79.7 | 10.4 | 74 | 11.2 | 204.8 | 228.8 | 204.8 | NO
| NG | 49 | 46 | 46 | 20 | 26.3 | 45.73 | 95 | 79.7 | 10.4 | 24.8 | 32.7 | 226.8 | 205 | 205 | NO
| NG | 47 | 51 | 51 | 20 | 68.5 | 13.38 | 95 | 79.7 | 10.4 | 64.3 | 16.6 | 206.1 | 225.7 | 206.1 | NO
| NG | 56 | 57 | 57 | 20 | 39.7 | 1.46 | 95 | 79.7 | 10.4 | 78 | 10.4 | 205.2 | 228.8 | 205.2 | NO
| NG | 46 | 45 | 45 | 24 | 27.4 | 45.73 | 50 | 79.7 | 10.4 | 24.8 | 32.6 | 226.8 | 206.3 | 206.3 | NO
| NG | 51 | 67 | 67 | 20 | 74 | 0.09 | 95 | 79.7 | 10.4 | 79.6 | 10.4 | 204.8 | 228.8 | 204.8 | NO
| NG | 51 | 3 | 4 | 20 | 80.4 | 13.29 | 50 | 79.7 | 10.4 | 64.4 | 16.6 | 206.1 | 225.2 | 206.1 | NO
| NG | 45 | 44 | 53 | 24 | 30.4 | 43.94 | 50 | 79.7 | 10.4 | 26.8 | 31.6 | 226.6 | 207.2 | 207.2 | NO
| NG | 45 | 54 | 55 | 20 | 29.7 | 1.69 | 95 | 79.7 | 10.4 | 77.6 | 11.2 | 205.2 | 228.7 | 205.2 | NO
| NG | 3 | 19 | 19 | 20 | 118.9 | 13.29 | 50 | 79.7 | 10.4 | 64.4 | 16.6 | 206.1 | 225.7 | 206.1 | NO
| NG | 44 | 21 | 22 | 39 | 59.4 | 37.95 | 50 | 79.7 | 10.4 | 33.7 | 20 | 226.1 | 203.6 | 203.6 | NO
| NG | 44 | 52 | 53 | 24 | 30.4 | 5.12 | 50 | 79.7 | 10.4 | 72.7 | 12.7 | 206.1 | 228.5 | 206.1 | NO
| NG | 54 | 55 | 55 | 20 | 29.7 | 0.34 | 95 | 79.7 | 10.4 | 79.3 | 10.4 | 205 | 228.8 | 205 | NO
| NG | 19 | 20 | 68 | 30 | 119.2 | 11.03 | 50 | 79.7 | 10.4 | [5 empty] | NO | TR_B sim: loading 0.1% despite baseline 10.4% (degenerate)
| NG | 21 | 22 | 22 | 39 | 59.4 | 37.95 | 50 | 79.7 | 10.4 | 33.7 | 20 | 226.1 | 203.6 | 203.6 | NO
| NG | 52 | 53 | 53 | 24 | 30.4 | 2.17 | 50 | 79.7 | 10.4 | 77 | 10.4 | 207.2 | 228.8 | 207.2 | NO
| NG | 20 | 29 | 68 | 30 | 119.2 | 8.76 | 50 | 79.7 | 10.4 | 69.4 | 11.5 | 205.4 | 225.5 | 205.4 | NO
| NG | 20 | 58 | 59 | 20 | 126 | 2.12 | 50 | 79.7 | 10.4 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 10.4% (degenerate)
| NG | 22 | 32 | 32 | 42 | 62.1 | 37.44 | 50 | 79.7 | 10.4 | 34.3 | 19.8 | 226 | 202.5 | 202.5 | NO
| NG | 29 | 17 | 68 | 30 | 119.2 | 6.47 | 50 | 79.7 | 10.4 | 72.2 | 11.5 | 205.4 | 225.5 | 205.4 | NO
| NG | 58 | 59 | 59 | 20 | 126 | 0.45 | 50 | 79.7 | 10.4 | 79.2 | 11.4 | 205 | 20 | 20 | NO
| NG | 32 | 33 | 33 | 29 | 64.7 | 36.62 | 50 | 79.7 | 10.4 | 35.2 | 19.4 | 225.8 | 201.9 | 201.9 | NO
| NG | 17 | 18 | 68 | 30 | 119.2 | 2.66 | 50 | 79.7 | 10.4 | 76.6 | 10.7 | 205 | 228.1 | 205 | NO
| NG | 17 | 63 | 63 | 42 | 148.7 | 1.76 | 50 | 79.7 | 10.4 | 77.7 | 11.3 | 205.3 | 226.7 | 205.3 | NO
| NG | 33 | 62 | 62 | 30 | 78.1 | 36.52 | 50 | 79.7 | 10.4 | 35.4 | 19.4 | 225.8 | 203.9 | 203.9 | NO
| NG | 18 | 24 | 68 | 30 | 119.2 | 1.02 | 50 | 79.7 | 10.4 | 78.6 | 10.7 | 205 | 228.1 | 205 | NO
| NG | 62 | 10 | 34 | 41 | 82.2 | 36.27 | 50 | 79.7 | 10.4 | 35.6 | 19.8 | 225.8 | 193.6 | 193.6 | NO
| NG | 24 | 25 | 25 | 30 | 121.9 | 0.52 | 50 | 79.7 | 10.4 | 79.1 | 10.7 | 205 | 228.2 | 205 | NO
| NG | 24 | 27 | 68 | 30 | 119.2 | 0.5 | 50 | 79.7 | 10.4 | 79.2 | 10.4 | 204.8 | 228.8 | 204.8 | NO
| NG | 10 | 9 | 6 | 41 | 114 | 28.22 | 50 | 79.7 | 10.4 | 45 | 18.8 | 224.3 | 197 | 197 | NO
| NG | 10 | 31 | 34 | 41 | 82.2 | 7.53 | 50 | 79.7 | 10.4 | 70 | 10.9 | 205.7 | 228.7 | 205.7 | NO
| NG | 25 | 26 | 26 | 30 | 123 | 0.52 | 50 | 79.7 | 10.4 | 79.1 | 10.4 | 205 | 228.8 | 205 | NO
| NG | 27 | 68 | 68 | 30 | 119.2 | 0.5 | 50 | 79.7 | 10.4 | 79.2 | 10.4 | 204.8 | 228.8 | 204.8 | NO
1 | OK | 9 | 11 | 6 | 41 | 114 | 19.15 | 50 | 79.7 | 10.4 | 54.9 | 15.5 | 218.9 | 211.2 | 211.2 | YES
2 | OK | 9 | 12 | 16 | 30 | 118.9 | 8.34 | 50 | 79.7 | 10.4 | 69 | 13.1 | 213 | 221.4 | 213 | YES
| NG | 31 | 34 | 34 | 41 | 82.2 | 7.13 | 50 | 79.7 | 10.4 | 71.1 | 10.8 | 204.9 | 228.7 | 204.9 | NO
3 | ** OPTIMAL ** | 11 | 8 | 6 | 41 | 114 | 13.33 | 50 | 79.7 | 10.4 | 57.6 | 14.9 | 218.3 | 213.2 | 213.2 | YES
| NG | 12 | 14 | 16 | 30 | 118.9 | 5.31 | 50 | 79.7 | 10.4 | 73 | 11.6 | 208.3 | 225.6 | 208.3 | NO
| NG | 34 | 42 | 42 | 41 | 83 | 5.13 | 50 | 79.7 | 10.4 | 73.5 | 10.8 | 205.3 | 228.7 | 205.3 | NO
| NG | 8 | 6 | 6 | 41 | 114 | 4.05 | 50 | 79.7 | 10.4 | 74.7 | 10.9 | 206.6 | 228.1 | 206.6 | NO
| NG | 14 | 16 | 16 | 30 | 118.9 | 2.49 | 50 | 79.7 | 10.4 | 76.4 | 11.6 | 208.9 | 225.6 | 208.9 | NO
| NG | 42 | 43 | 43 | 41 | 89.3 | 3.67 | 50 | 79.7 | 10.4 | 75.2 | 10.8 | 205.8 | 228.7 | 205.8 | NO
| NG | 6 | 5 | 5 | 41 | 114.5 | 2.89 | 50 | 79.7 | 10.4 | 76.1 | 10.9 | 207.1 | 228.2 | 207.1 | NO
| NG | 16 | 23 | 23 | 30 | 136.2 | 2.49 | 50 | 79.7 | 10.4 | 76.4 | 11.6 | 208.9 | 225.6 | 208.9 | NO
| NG | 43 | 40 | 40 | 41 | 90.8 | 2.8 | 50 | 79.7 | 10.4 | 76.4 | 10.4 | 204.6 | 228.8 | 204.6 | NO
| NG | 40 | 41 | 41 | 41 | 91.8 | 2.8 | 50 | 79.7 | 10.4 | 76.4 | 10.4 | 204.6 | 228.8 | 204.6 | NO
| NG | 41 | 39 | 39 | 41 | 107.6 | 2.8 | 50 | 79.7 | 10.4 | 76.4 | 10.4 | 204.6 | 228.8 | 204.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 67-035828
TR_B (available) | 67-021521
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 79.7
TR_B Baseline Loading% | 10.4
Total Scenarios Evaluated | 49
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 8
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 41
Tie Line Distance (m) | 114
Load Transferred (kW) | 13.33
TR_A Loading After (%) | 57.6
TR_B Loading After (%) | 14.9
Minimum Voltage (V) | 213.2