## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 39 | 36 | 30 | 25 | 26.6 | 7.47 | 50 | 87.3 | 49.4 | 58.4 | 78.9 | 217 | 216.7 | 216.7 | YES
2 | OK | 39 | 17 | 18 | 17 | 6.5 | 3.23 | 50 | 87.3 | 49.4 | 74.9 | 57.8 | 214.7 | 218.3 | 214.7 | YES
| NG | 7 | 5 | 5 | 24 | 143 | 8.13 | 50 | 87.3 | 49.4 | 55.5 | 81.6 | 221.1 | 212 | 212 | NO
3 | ** OPTIMAL ** | 36 | 35 | 30 | 25 | 26.6 | 6.47 | 50 | 87.3 | 49.4 | 62.2 | 74.9 | 216.8 | 217.2 | 216.8 | YES
4 | OK | 17 | 12 | 18 | 17 | 6.5 | 3.23 | 50 | 87.3 | 49.4 | 74.9 | 57.8 | 214.7 | 218.3 | 214.7 | YES
5 | OK | 5 | 4 | 4 | 24 | 145.1 | 7.4 | 50 | 87.3 | 49.4 | 58.3 | 78.9 | 221.1 | 212 | 212 | YES
| NG | 35 | 34 | 30 | 25 | 26.6 | 6.47 | 50 | 87.3 | 49.4 | [5 empty] | NO | TR_B sim: not converged
6 | OK | 12 | 13 | 18 | 17 | 6.5 | 2.43 | 50 | 87.3 | 49.4 | 78 | 54.6 | 214.1 | 220 | 214.1 | YES
7 | OK | 4 | 45 | 45 | 24 | 190.5 | 7.4 | 50 | 87.3 | 49.4 | 58.3 | 78.6 | 221.1 | 213.8 | 213.8 | YES
8 | OK | 34 | 40 | 30 | 25 | 26.6 | 3.38 | 50 | 87.3 | 49.4 | 74.1 | 62.6 | 215.5 | 220.3 | 215.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-035940
TR_B (available) | 64-008078
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 87.3
TR_B Baseline Loading% | 49.4
Total Scenarios Evaluated | 10
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 36
Switch Child Node | 35
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 26.6
Load Transferred (kW) | 6.47
TR_A Loading After (%) | 62.2
TR_B Loading After (%) | 74.9
Minimum Voltage (V) | 216.8