## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 17 | 11 | 11 | 1 | 77.4 | 13.31 | 50 | 87.6 | 34 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 17 | 27 | 31 | 41 | 7.4 | 9.32 | 50 | 87.6 | 34 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 11 | 12 | 12 | 1 | 82.5 | 13.06 | 50 | 87.6 | 34 | 36.8 | 50.1 | 224.6 | 208.9 | 208.9 | NO
1 | OK | 27 | 26 | 31 | 41 | 7.4 | 9.03 | 50 | 87.6 | 34 | 52.8 | 44.5 | 218.7 | 222.3 | 218.7 | YES
| NG | 12 | 34 | 34 | 1 | 86.4 | 12.88 | 50 | 87.6 | 34 | 37.5 | 49.9 | 224.6 | 209.4 | 209.4 | NO
2 | OK | 26 | 25 | 31 | 41 | 7.4 | 7.14 | 50 | 87.6 | 34 | 60 | 42.3 | 218.7 | 223.1 | 218.7 | YES
| NG | 34 | 5 | 5 | 1 | 100.5 | 12.74 | 50 | 87.6 | 34 | 38 | 49.7 | 224.5 | 209.7 | 209.7 | NO
3 | OK | 25 | 14 | 31 | 41 | 7.4 | 7 | 50 | 87.6 | 34 | 60 | 42.1 | 218.7 | 223.1 | 218.7 | YES
| NG | 5 | 6 | 16 | 69 | 106.4 | 12.4 | 50 | 87.6 | 34 | 39.3 | 42.4 | 224.5 | 205.8 | 205.8 | NO
4 | ** OPTIMAL ** | 14 | 13 | 31 | 41 | 7.4 | 6.92 | 50 | 87.6 | 34 | 60.9 | 42 | 218.7 | 223.1 | 218.7 | YES
| NG | 6 | 7 | 16 | 69 | 106.4 | 9.57 | 50 | 87.6 | 34 | 50.2 | 42.4 | 222.4 | 205.8 | 205.8 | NO
5 | OK | 13 | 22 | 31 | 41 | 7.4 | 5.39 | 50 | 87.6 | 34 | 66.8 | 40.2 | 218.6 | 223.1 | 218.6 | YES
| NG | 7 | 8 | 16 | 69 | 106.4 | 8.92 | 50 | 87.6 | 34 | 52.6 | 41.8 | 222.2 | 207 | 207 | NO
6 | OK | 22 | 21 | 31 | 41 | 7.4 | 4.6 | 50 | 87.6 | 34 | 69.8 | 39.3 | 218.6 | 223.1 | 218.6 | YES
| NG | 8 | 18 | 16 | 69 | 106.4 | 7.34 | 50 | 87.6 | 34 | 52.6 | 41.8 | 222.2 | 207 | 207 | NO
7 | OK | 21 | 33 | 31 | 41 | 7.4 | 3.66 | 50 | 87.6 | 34 | 73.4 | 38.2 | 217.9 | 223.4 | 217.9 | YES
| NG | 18 | 19 | 16 | 69 | 106.4 | 7.34 | 50 | 87.6 | 34 | 58.8 | 41.8 | 221 | 207 | 207 | NO
| NG | 19 | 20 | 16 | 69 | 106.4 | 7.09 | 50 | 87.6 | 34 | 58.8 | 41.8 | 221 | 207 | 207 | NO
| NG | 20 | 37 | 16 | 69 | 106.4 | 6.38 | 50 | 87.6 | 34 | 62.5 | 41.8 | 219.1 | 207 | 207 | NO
| NG | 37 | 36 | 16 | 69 | 106.4 | 6.12 | 50 | 87.6 | 34 | 63.6 | 41.8 | 218.6 | 207 | 207 | NO
| NG | 36 | 46 | 16 | 69 | 106.4 | 6.12 | 50 | 87.6 | 34 | 63.6 | 41.8 | 218.6 | 207 | 207 | NO
| NG | 46 | 16 | 16 | 69 | 106.4 | 6.06 | 50 | 87.6 | 34 | 63.8 | 41.8 | 218.6 | 207.2 | 207.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 68-003151
TR_B (available) | 51-940348
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 87.6
TR_B Baseline Loading% | 34
Total Scenarios Evaluated | 22
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 13
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 41
Tie Line Distance (m) | 7.4
Load Transferred (kW) | 6.92
TR_A Loading After (%) | 60.9
TR_B Loading After (%) | 42
Minimum Voltage (V) | 218.7