## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 66 | 81 | 81 | 3 | 148.2 | 33.38 | 50 | 85.3 | 12.4 | 57.1 | 94.3 | 199.6 | 203.2 | 199.6 | NO
| NG | 66 | 6 | 6 | 3 | 146.6 | 16.56 | 50 | 85.3 | 12.4 | 73 | 39.7 | 197.5 | 210.5 | 197.5 | NO
| NG | 37 | 39 | 44 | 4 | 28 | 19.13 | 50 | 85.3 | 12.4 | 71.1 | 57.1 | 199.2 | 216.8 | 199.2 | NO
| NG | 39 | 72 | 44 | 4 | 28 | 18.58 | 50 | 85.3 | 12.4 | 71.5 | 55.8 | 199.2 | 216.8 | 199.2 | NO
| NG | 72 | 27 | 44 | 4 | 28 | 18.58 | 50 | 85.3 | 12.4 | 71.5 | 55.8 | 199.2 | 216.8 | 199.2 | NO
| NG | 33 | 32 | 32 | 3 | 52.8 | 29.55 | 50 | 85.3 | 12.4 | 61.8 | 84 | 218.6 | 202.2 | 202.2 | NO
| NG | 32 | 31 | 21 | 7 | 68.7 | 27.03 | 50 | 85.3 | 12.4 | 63.8 | 77 | 216.1 | 206.2 | 206.2 | NO
1 | ** OPTIMAL ** | 31 | 1 | 21 | 7 | 68.7 | 17.08 | 50 | 85.3 | 12.4 | 71.4 | 52.4 | 214.2 | 216.7 | 214.2 | YES
| NG | 1 | 24 | 24 | 3 | 123.5 | 8.75 | 50 | 85.3 | 12.4 | 77.9 | 33.2 | 207.9 | 216.3 | 207.9 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 68-011120
TR_B (available) | 64-006651
TR_A Rated kVA | 160
TR_B Rated kVA | 50
TR_A Baseline Loading% | 85.3
TR_B Baseline Loading% | 12.4
Total Scenarios Evaluated | 9
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 31
Switch Child Node | 1
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 68.7
Load Transferred (kW) | 17.08
TR_A Loading After (%) | 71.4
TR_B Loading After (%) | 52.4
Minimum Voltage (V) | 214.2